## frame format
Frame format
PWS2-30K-NA supports RS485 or Ethernet， When implementing RS485, the baud rate is19200bps, verification: Modbus RTU Crc16 When deploying ethernet, the communication format conforms to ModBusTCP。
Reading format
Sending frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | register quantity H | register quantity L | Verification
(L->H)
0x01 | 0x03 | 0x00 | 0x00 | 0x00 | 0x0A | CRC
Response frame
Device address | Operation code | data quantily | data 1 | …… | data N | Verification
|  | (register quantity*2) |  |  |  | (L->H)
0x01 | 0x03 | 0x14(N) | XX | …… | XX | CRC
Writing format
Sending frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC
Response frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x01 | 0x06 | 0x00 | 0x06 | 0x00 | 0x03 | CRC

## Pcs30kW-COMM_PROTOCOL_V101
| Start | End | Size | Access | Register Name | 寄存器名称 | Type | Units | Comments | Magnification Actual Value=Regiser Data ÷ Magnification | Range | Default(Actual Value) | Remark
0x0001 | 1 | 16 | 16 | R | model |  | String(32) |  | Manufacturer and model number
0x0011 | 17 | 24 | 8 | R | serial |  | String(16) |  | Serial Number
0x0020 | 32 | 32 | 1 | R | fault_occurred_0 |  | uint16x |  | Faults 15:0 occured
0x0021 | 33 | 33 | 1 | R | fault_occurred_1 |  | uint16x |  | Faults 31:16 occured
0x0022 | 34 | 34 | 1 | R | fault_occurred_2 |  | uint16x |  | Faults 47:32 occured
0x0023 | 35 | 35 | 1 | R | fault_occurred_3 |  | uint16x |  | Faults 63:48 occured
0x0024 | 36 | 36 | 1 | R | fault_occurred_4 |  | uint16x |  | Faults 79:64 occured
0x0025 | 37 | 37 | 1 | R | fault_occurred_5 |  | uint16x |  | Faults 95:80 occured
0x0026 | 38 | 38 | 1 | R | fault_occurred_6 |  | uint16x |  | Faults 111:96 occured
0x0027 | 39 | 39 | 1 | R | fault_occurred_7 |  | uint16x |  | Faults 127:112 occurred
0x0028 | 40 | 40 | 1 | R | fault_occurred_8 |  | uint16x |  | Faults 143:128 occurred
0x0029 | 41 | 41 | 1 | R | fault_occurred_9 |  | uint16x |  | Faults 159:144 occured
0x002A | 42 | 42 | 1 | R | fault_occurred_10 |  | uint16x |  | Faults 175:160 occured
0x002B | 43 | 43 | 1 | R | fault_occurred_11 |  | uint16x |  | Faults 191:176 occured
0x002C | 44 | 44 | 1 | R | fault_occurred_12 |  | uint16x |  | Faults 207:192 occured
0x002D | 45 | 45 | 1 | R | fault_occurred_13 |  | uint16x |  | Faults 223:208 occured
0x002E | 46 | 46 | 1 | R | fault_occurred_14 |  | uint16x |  | Faults 239:224 occured
0x002F | 47 | 47 | 1 | R | fault_occurred_15 |  | uint16x |  | Faults 255:240 occurred
0x0030 | 48 | 48 | 1 | R | fault_occurred_16 |  | uint16x |  | Faults 271:256 occured
0x0031 | 49 | 49 | 1 | R | fault_occurred_17 |  | uint16x |  | Faults 287:272 occured
0x0032 | 50 | 50 | 1 | R | fault_occurred_18 |  | uint16x |  | Faults 303:288 occured
0x0033 | 51 | 51 | 1 | R | fault_occurred_19 |  | uint16x |  | Faults 319:304 occured
0x0034 | 52 | 52 | 1 | R | fault_occurred_20 |  | uint16x |  | Faults 335:320 occured
0x0035 | 53 | 53 | 1 | R | fault_occurred_21 |  | uint16x |  | Faults 351:336 occured
0x0036 | 54 | 54 | 1 | R | fault_occurred_22 |  | uint16x |  | Faults 367:352 occured
0x0037 | 55 | 55 | 1 | R | fault_occurred_23 |  | uint16x |  | Faults 383:368 occurred
0x0038 | 56 | 56 | 1 | R | fault_occurred_24 |  | uint16x |  | Faults 399:384 occured
0x0039 | 57 | 57 | 1 | R | fault_occurred_25 |  | uint16x |  | Faults 415:400 occured
0x003A | 58 | 58 | 1 | R | fault_occurred_26 |  | uint16x |  | Faults 431:416 occured
0x003B | 59 | 59 | 1 | R | fault_occurred_27 |  | uint16x |  | Faults 447:432 occured
0x003C | 60 | 60 | 1 | R | fault_occurred_28 |  | uint16x |  | Faults 463:448 occured
0x003D | 61 | 61 | 1 | R | fault_occurred_29 |  | uint16x |  | Faults 479:464 occured
0x003E | 62 | 62 | 1 | R | fault_occurred_30 |  | uint16x |  | Faults 495:480 occured
0x003F | 63 | 63 | 1 | R | fault_occurred_31 |  | uint16x |  | Faults 512:496 occurred
0x0065 | 101 | 101 | 1 | R | InvOutVolt_A _Rms_Value |  | uint16 | V | AC A-B RMS voltage | ×10
0x0066 | 102 | 102 | 1 | R | InvOutVolt_B _Rms_Value |  | uint16 | V | AC B-C RMS voltage | ×10
0x0067 | 103 | 103 | 1 | R | InvOutVolt_C_Rms_value |  | uint16 | V | AC C-A RMS voltage | ×10
0x0068 | 104 | 104 | 1 | R | Analog_A_GridCurrent_Rms_Value |  | uint16 | A | AC phA RMS current | ×10
0x0069 | 105 | 105 | 1 | R | Analog_B_GridCurrent_Rms_Value |  | uint16 | A | AC phB RMS current | ×10
0x006A | 106 | 106 | 1 | R | Analog_C_GridCurrent_Rms_Value |  | uint16 | A | AC phC RMS current | ×10
0x006B | 107 | 107 | 1 | R | Analog_GridCurrent_Freq |  | uint16 | Hz | AC frequency | ×100
0x006E | 110 | 110 | 1 | R | Analog_A_ActivePower_Rms_Value |  | int16 | kW | AC phA Real Power | ×100
0x006F | 111 | 111 | 1 | R | Analog_B_ActivePower_Rms_Value |  | int16 | kW | AC phB Real Power | ×100
0x0070 | 112 | 112 | 1 | R | Analog_C_ActivePower_Rms_Value |  | int16 | kW | AC phC Real Power | ×100
0x0071 | 113 | 113 | 1 | R | Analog_A_ReactivePower_Rms_Value |  | int16 | kVAR | AC phA Reactive Power | ×100
0x0072 | 114 | 114 | 1 | R | Analog_B_ReactivePower_Rms_Value |  | int16 | kVAR | AC phB Reactive Power | ×100
0x0073 | 115 | 115 | 1 | R | Analog_C_ReactivePower_Rms_Value |  | int16 | kVAR | AC phC Reactive Power | ×100
0x0074 | 116 | 116 | 1 | R | Analog_A_ApparentPower |  | int16 | kVA | AC phA Apparent Power | ×100
0x0075 | 117 | 117 | 1 | R | Analog_B_ApparentPower |  | int16 | kVA | AC phB Apparent Power | ×100
0x0076 | 118 | 118 | 1 | R | Analog_C_ApparentPower |  | int16 | kVA | AC phC Apparent Power | ×100
0x0077 | 119 | 119 | 1 | R | Analog_A_PF_Rms_Value |  | int16 | PF | AC phA Power Factor | ×100
0x0078 | 120 | 120 | 1 | R | Analog_B_PF_Rms_Value |  | int16 | PF | AC phB Power Factor | ×100
0x0079 | 121 | 121 | 1 | R | Analog_C_PF_Rms_Value |  | int16 | PF | AC phC Power Factor | ×100
0x007A | 122 | 122 | 1 | R | Analog_ ActivePower_3Phase |  | int16 | kW | AC Real Power | ×1
0x007B | 123 | 123 | 1 | R | Analog_ ReactivePower_3Phase |  | int16 | kVAR | AC Reactive Power | ×1
0x007C | 124 | 124 | 1 | R | Analog_ ApparentPower_3Phase |  | uint16 | kVA | AC Apparent Power | ×1
0x007D | 125 | 125 | 1 | R | Analog_ PowerFactor_3Phase |  | int16 | PF | AC Power Factor | ×1
0x007E | 126 | 127 | 2 | RW | Analog_Chg_Energy |  | uint32 | kWh | AC charged energy | ×1
0x0080 | 128 | 129 | 2 | RW | Analog_Dischg_Energy |  | uint32 | kWh | AC discharged energy | ×1
0x0082 | 130 | 131 | 2 | R | Analog_Reactive_Energy |  | uint32 | kWh | Reactive energy | ×1
0x0084 | 132 | 132 | 1 | R | Temperature_Of_AC_ Heat_Sink |  | int16 | C | Temperature of AC heat sink | ×1
0x0085 | 133 | 133 | 1 | R | Positive_BUS_Voltage |  | uint16 | V | BUS+ side voltage | ×10
0x0086 | 134 | 134 | 1 | R | Negtive_BUS_Voltage |  | uint16 | V | BUS- side voltage | ×10
0x0087 | 135 | 135 | 1 | RW | Target_Active_Power |  | int16 | kW | Target active power | ×10 | -30.0kW ~30.0kW | 0 | minus: discharge, positive: charge
0x0088 | 136 | 136 | 1 | RW | Target_Reactive_Power |  | int16 | kVAR | Target reactive power | ×10 | -30.0kVar~30.0kVar | 0 | minus: inductive, positive: capacitive
0x0089 | 137 | 137 | 1 | RW | Target_Off-grid_Voltage |  | uint16 |  | Target off-grid voltage bias | ×100 | -0.10~0.10(to rated voltage) | 0
0x008A | 138 | 138 | 1 | RW | Target_Off-grid_Frequency |  | int16 | Hz | Target off-grid frequency bias | ×100 | -2.0~2.0Hz | 0
0x008D | 141 | 141 | 1 | R | Analog_DC_Power |  | int16 | kW | DC power | ×100
0x008E | 142 | 142 | 1 | R | Analog_DC_Voltage |  | uint16 | V | DC voltage | ×10
0x008F | 143 | 143 | 1 | R | Analog_DC_Current |  | uint16 | A | DC current | ×10
0x0090 | 144 | 145 | 2 | RW | Analog_DC_Chg_Energy |  | uint32 | kWh | DC charged energy | ×1
0x0092 | 146 | 147 | 2 | RW | Analog_ DC_Dischg_Energy |  | uint32 | kWh | DC discharged energy | ×1
0x0094 | 148 | 148 | 1 | R | Temperature_Of_DCDC_Heat_Sink |  | int16x | C | Temperature of DC heat sink | ×1
0x00A8 | 168 | 168 | 1 | R | D.C._Voltage |  | uint16 | V | D.C. Voltage |  |  |  |  | Vendor B protocol is only for transferring the data from BMS via RS485 to EMS via Ethernet, no protection will be applied by inverter. Vendor A protocol provides protection and status display by inverter
0x00A9 | 169 | 169 | 1 | R | D.C._Voltage_SF |  | sunssf | SF | D.C. Voltage SF |  |  |  | BMS protocol for Vendor B
0x00AA | 170 | 170 | 1 | R | D.C._Current |  | uint16 | A | D.C. Current |  |  |  | BMS protocol for Vendor B
0x00AB | 171 | 171 | 1 | R | D.C._Current_SF |  | sunssf | SF | D.C. Current SF |  |  |  | BMS protocol for Vendor B
0x00AC | 172 | 172 | 1 | R | average_temp |  | uint16 | C | average temp |  |  |  | BMS protocol for Vendor B
0x00AD | 173 | 173 | 1 | R | average_temp_SF |  | sunssf | SF | average temp SF |  |  |  | BMS protocol for Vendor B
0x00AE | 174 | 174 | 1 | R | max_temp |  | uint16 | C | max temp |  |  |  | BMS protocol for Vendor B
0x00AF | 175 | 175 | 1 | R | max_temp_SF |  | sunssf | SF | max temp SF |  |  |  | BMS protocol for Vendor B
0x00B0 | 176 | 176 | 1 | R | min_Temp |  | uint16 | C | min Temp |  |  |  | BMS protocol for Vendor B
0x00B1 | 177 | 177 | 1 | R | min_Temp_SF |  | sunssf | SF | min Temp SF |  |  |  | BMS protocol for Vendor B
0x00B2 | 178 | 178 | 1 | R | max_cell_volt |  | uint16 | V | max cell volt |  |  |  | BMS protocol for Vendor B
0x00B3 | 179 | 179 | 1 | R | max_cell_volt_SF |  | sunssf | SF | max cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B4 | 180 | 180 | 1 | R | min_cell_volt |  | uint16 | V | min cell volt |  |  |  | BMS protocol for Vendor B
0x00B5 | 181 | 181 | 1 | R | min_cell_volt_SF |  | sunssf | SF | min cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B6 | 182 | 182 | 1 | R | average_cell_volt |  | uint16 | V | average cell volt |  |  |  | BMS protocol for Vendor B
0x00B7 | 183 | 183 | 1 | R | average_cell_volt_SF |  | sunssf | SF | average cell volt SF |  |  |  | BMS protocol for Vendor B
0x00B8 | 184 | 184 | 1 | R | soc |  | uint16 |  | SOC |  |  |  | BMS protocol for Vendor B
0x00B9 | 185 | 185 | 1 | R | soc_SF |  | sunssf | SF | soc SF |  |  |  | BMS protocol for Vendor B
0x00BA | 186 | 186 | 1 | R | soh |  | uint16 |  | SOC |  |  |  | BMS protocol for Vendor B
0x00BB | 187 | 187 | 1 | R | soh_SF |  | sunssf | SF | soh SF |  |  |  | BMS protocol for Vendor B
0x012C | 300 | 303 | 4 | RW | IP_Address |  | uint64 |  | IP addreess |  |  |  | take effect after hard reset
0x0130 | 304 | 307 | 4 | RW | Netmask |  | uint64 |  | Netmask |  |  |  | take effect after hard reset
0x0134 | 308 | 311 | 4 | RW | Gateway |  | uint64 |  | Gateway IP address |  |  |  | take effect after hard reset
0x0138 | 312 | 314 | 3 | RW | MAC |  | uint48 |  | MAC address |  | first 2 bytes fixed as 00-24, the following 4 bytes is changeable, |  | take effect after hard reset
0x013C | 316 | 316 | 1 | RW | Modbus_Device_Address |  | uint16 |  | Modbus device address |  | 1~247 | 1 | take effect after hard reset
0x0140 | 320 | 320 | 1 | RW | baud_Rate |  | enum16 |  | Interface baud rate in bits per second |  | 0: 19200, 1: 9600 | 0 | take effect after hard reset
0x0145 | 325 | 325 | 1 | RW | Interface Type |  | enum16 |  | Interface type |  | 0: RS-485, 1: Ethernet | 0
0x0146 | 326 | 326 | 1 | RW | Protocol_Selection | 选择通讯协议 | enum16 |  | Serial protocol selection |  | 0: old protocol 1: sunspec | 1
0x0147 | 327 | 327 | 1 | RW | EMS timeout setting |  | uint16 | s |  | ×1 | 0~32767 | 0
0x0148 | 328 | 328 | 1 | RW | EPO enable/disable |  | enum16 |  | EPO enableing |  | 0: disabled, 1: enabled | 0
0x0149 | 329 | 329 | 1 | RW | BMS timeout setting |  | uint16 | s |  | ×1 | 0~32767 | 0
0x01F4 | 500 | 501 | 2 | R | SunSpec_ID |  | uint32x |  | Well-known value. Uniquely identifies this as a SunSpec Modbus Map
0x01F6 | 502 | 502 | 1 | R | SunSpec_DID_0001 |  | uint16 |  | Uniquely identifies this as a SunSpec Common Model Block
0x01F7 | 503 | 503 | 1 | R | SunSpec_Length_0001 |  | uint16 |  | Length of block in 16-bit registers
0x01F8 | 504 | 519 | 16 | R | Manufacturer |  | string |  | Manufacturer
0x0208 | 520 | 535 | 16 | R | Model |  | string |  | Manufacturer specific value (32 chars)
0x0218 | 536 | 543 | 8 | R | Options |  | string |  | Manufacturer specific value (16 chars) |  | 波特率+数据位+停止位+校验位
0x0220 | 544 | 551 | 8 | R | Version |  | string |  | Manufacturer specific value (16 chars)
0x0228 | 552 | 567 | 16 | R | Serial Number |  | string |  | Manufacturer specific value (32 chars)
0x0238 | 568 | 568 | 1 | RW | Device Address |  | uint16 |  | Modbus device address
0x0239 | 569 | 569 | 1 | R | pad |  | pad |  | Force even alignment
0x023A | 570 | 570 | 1 | R | SunSpec_DID_0103 |  | uint16 |  | 103 - 3-phase inverter
0x023B | 571 | 571 | 1 | R | SunSpec_Length_0103 |  | uint16 |  | Length of model block in registers
0x023C | 572 | 572 | 1 | R | Amps |  | uint16 | A | AC Current
0x023D | 573 | 573 | 1 | R | Amps PhaseA |  | uint16 | A | Phase A Current
0x023E | 574 | 574 | 1 | R | Amps PhaseB |  | uint16 | A | Phase B Current
0x023F | 575 | 575 | 1 | R | Amps PhaseC |  | uint16 | A | Phase C Current
0x0240 | 576 | 576 | 1 | R | A_SF |  | sunssf | SF | AC Current Scale factor
0x0241 | 577 | 577 | 1 | R | PPVphAB |  | uint16 | V | Phase Voltage AB
0x0242 | 578 | 578 | 1 | R | PPVphBC |  | uint16 | V | Phase Voltage BC
0x0243 | 579 | 579 | 1 | R | PPVphCA |  | uint16 | V | Phase Voltage CA
0x0244 | 580 | 580 | 1 | R | PhVphA |  | uint16 | V | Phase Voltage AN
0x0245 | 581 | 581 | 1 | R | PhVphB |  | uint16 | V | Phase Voltage BN
0x0246 | 582 | 582 | 1 | R | PhVphC |  | uint16 | V | Phase Voltage CN
0x0247 | 583 | 583 | 1 | R | V_SF |  | sunssf | SF | AC Voltage Scale factor
0x0248 | 584 | 584 | 1 | R | Watts |  | int16 | W | AC Power
0x0249 | 585 | 585 | 1 | R | W_SF |  | sunssf | SF | AC Power Scale factor
0x024A | 586 | 586 | 1 | R | Hz |  | uint16 | Hz | Line Frequency
0x024B | 587 | 587 | 1 | R | Hz_SF |  | sunssf | SF | Scale factor
0x024C | 588 | 588 | 1 | R | VA |  | int16 | VA | AC Apparent Power
0x024D | 589 | 589 | 1 | R | VA_SF |  | sunssf | SF | Scale factor
0x024E | 590 | 590 | 1 | R | VAr |  | int16 | var | AC Reactive Power
0x024F | 591 | 591 | 1 | R | VAr_SF |  | sunssf | SF | Scale factor
0x0250 | 592 | 592 | 1 | R | PF |  | int16 | Pct | AC Power Factor
0x0251 | 593 | 593 | 1 | R | PF_SF |  | sunssf | SF | Scale factor
0x0252 | 594 | 595 | 2 | R | WattHours |  | acc32 | Wh | AC Energy
0x0254 | 596 | 596 | 1 | R | WH_SF |  | sunssf | SF | Scale factor
0x0255 | 597 | 597 | 1 | R | DC Amps |  | int16 | A | DC Current | X10
0x0256 | 598 | 598 | 1 | R | DCA_SF |  | sunssf | SF | Scale factor
0x0257 | 599 | 599 | 1 | R | DC Voltage |  | uint16 | V | DC Voltage
0x0258 | 600 | 600 | 1 | R | DCV_SF |  | sunssf | SF | Scale factor
0x0259 | 601 | 601 | 1 | R | DC Watts |  | int16 | W | DC Power | ×100
0x025A | 602 | 602 | 1 | R | DCW_SF |  | sunssf | SF | Scale factor
0x025B | 603 | 603 | 1 | R | Cabinet Temperature |  | int16 | C | Cabinet Temperature
0x025C | 604 | 604 | 1 | R | Heat Sink Temperature |  | int16 | C | Heat Sink Temperature |  |  |  | DCAC circuit heat sink
0x025D | 605 | 605 | 1 | R | Transformer Temperature |  | int16 | C | Transformer Temperature |  |  |  | No transformer
0x025E | 606 | 606 | 1 | R | Other Temperature |  | int16 | C | Other Temperature |  |  |  | DCDC circuit heat sink
0x025F | 607 | 607 | 1 | R | Tmp_SF |  | sunssf |  | Scale factor
0x0260 | 608 | 608 | 1 | R | Operating State |  | enum16 |  | Enumerated value. Operating state
0x0261 | 609 | 609 | 1 | R | Vendor Operating State |  | enum16 |  | Vendor specific operating state code
0x0262 | 610 | 611 | 2 | R | Event1 |  | bitfield32 |  | Bitmask value. Event fields
0x0264 | 612 | 613 | 2 | R | Event Bitfield 2 |  | bitfield32 |  | Vendor defined events |  |  |  | Faults 95:64 occured
0x0266 | 614 | 615 | 2 | R | Vendor Event Bitfield 1 |  | bitfield32 |  | Vendor defined events |  |  |  | Faults 127:96 occured
0x0268 | 616 | 617 | 2 | R | Vendor Event Bitfield 2 |  | bitfield32 |  | Vendor defined events |  |  |  | Faults 159:128 occurred
0x026A | 618 | 619 | 2 | R | Vendor Event Bitfield 3 |  | bitfield32 |  | Vendor defined events |  |  |  | Faults 191:160 occured
0x026C | 620 | 621 | 2 | R | Vendor Event Bitfield 4 |  | bitfield32 |  | Vendor defined events |  |  |  | Faults 223:192 occured
0x026E | 622 | 622 | 1 | R | SunSpec_DID_FFFF |  | uint16 |  | SunSpec End Block
0x026F | 623 | 623 | 1 | R | SunSpec_Length_FFFF |  | uint16 |  | Length of End Block
0x028A | 650 | 650 | 1 | RW | SETDATA_ModOnCmd |  | uint16 |  |  |  | 0: false, 1 true
0x028B | 651 | 651 | 1 | RW | SETDATA_ModOffCmd |  | uint16 |  |  |  | 0: false, 1 true
0x028C | 652 | 652 | 1 | RW | SETDATA_ClearFailureCmd |  | uint16 |  |  |  | 0: false, 1 true
0x028D | 653 | 653 | 1 | RW | SETDATA_OnGridCmd |  | uint16 |  |  |  | 0: false, 1 true
0x028E | 654 | 654 | 1 | RW | SETDATA_OffGridCmd |  | uint16 |  |  |  | 0: false, 1 true
0x02EC | 748 | 748 | 1 | R | Output voltage |  | enum16 |  |  |  | 0: 380V, 1: 400V, 2: 480V | 0
0x02ED | 749 | 749 | 1 | R | Output frequency |  | enum16 |  |  |  | 0: 50Hz, 1 60Hz, | 0
0x02EE | 750 | 750 | 1 | R | Grid type |  | enum16 |  |  |  | 0: 3P4W, 1: 3P3W, | 0
0x02F1 | 753 | 753 | 1 | R | output power Rating |  | enum16 |  |  |  | 0: 10kW, 1: 20kW, 2: 30kW, 3: 29kW | 2
0x0300 | 768 | 768 | 1 | RW | ac_ov_trip_level_1 |  | uint16 | V |  | ×100 | 1.05~1.2 | 1.1
0x0301 | 769 | 769 | 1 | RW | ac_ov_trip_time_1 |  | uint16 | s |  | ×100 | 0~13s | 1
0x0302 | 770 | 770 | 1 | RW | ac_ov_trip_level_2 |  | uint16 | V |  | ×100 | 1.05~1.2 | 1.1
0x0303 | 771 | 771 | 1 | RW | ac_ov_trip_time_2 |  | uint16 | s |  | ×100 | 0~0.16s | 0.16
0x0304 | 772 | 772 | 1 | RW | ac_uv_trip_level_1 |  | uint16 | V |  | ×100 | 0. 45~0.95 | 0.88
0x0305 | 773 | 773 | 1 | RW | ac_uv_trip_time_1 |  | uint16 | s |  | ×100 | 0~21s | 2
0x0306 | 774 | 774 | 1 | RW | ac_uv_trip_level_2 |  | uint16 | V |  | ×100 | 0. 45~0.95 | 0.6
0x0307 | 775 | 775 | 1 | RW | ac_uv_trip_time_2 |  | uint16 | s |  | ×100 | 0~11s | 1
0x0308 | 776 | 776 | 1 | RW | ac_uv_trip_level_3 |  | uint16 | V |  | ×100 | 0.45~0.95 | 0.45
0x0309 | 777 | 777 | 1 | RW | ac_uv_trip_time_3 |  | uint16 | s |  | ×100 | 0~0.16s | 0.16
0x030A | 778 | 778 | 1 | RW | ac_of_trip_level_1 |  | uint16 | Hz |  | ×100 | 0~4.5Hz | 0.5
0x030B | 779 | 779 | 1 | RW | ac_of_trip_time_1 |  | uint16 | s |  | ×100 | 0-300s | 2
0x030C | 780 | 780 | 1 | RW | ac_of_trip_level_2 |  | uint16 | Hz |  | ×100 | 0~4.5Hz | 2
0x030D | 781 | 781 | 1 | RW | ac_of_trip_time_2 |  | uint16 | s |  | ×100 | 0~10s | 0.16
0x030E | 782 | 782 | 1 | RW | ac_uf_trip_level_1 |  | uint16 | Hz |  | ×100 | -0~4.5Hz | -1
0x030F | 783 | 783 | 1 | RW | ac_uf_trip_time_1 |  | uint16 | s |  | ×100 | 0-300s | 2
0x0310 | 784 | 784 | 1 | RW | ac_uf_trip_level_2 |  | uint16 | Hz |  | ×100 | -0~4.5Hz | -2
0x0311 | 785 | 785 | 1 | RW | ac_uf_trip_time_2 |  | uint16 | s |  | ×100 | 0~10s | 0.16
0x0312 | 786 | 786 | 1 | RW | reconnect_time |  | uint16 | s |  | ×1 |  | 50
0x0313 | 787 | 787 | 1 | RW | Active power adjustment by frequency |  | enum16 |  |  |  | 0: disabled, 1: enabled
0x0314 | 788 | 788 | 1 | RW | Power adjustment by voltage |  | enum16 |  |  |  | 0: disabled, 1: Active regulation, 2: Reactive regulation
0x0315 | 789 | 789 | 1 | RW | Reactive power adjustment by active power |  | enum16 |  |  |  | 0: disabled, 1: enabled
0x0316 | 790 | 790 | 1 | RW | Anti-islanding |  | enum16 |  |  |  | 0: disabled, 1: enabled
0x0317 | 791 | 791 | 1 | RW | Ride-Through function | 电压频率穿越使能 | enum16 |  |  |  | 0: Disabled 1: Enabled
0x0318 | 792 | 792 | 1 | RW | Reactive Power Regulation Mode | 无功调节模式 | enum16 |  |  |  | 0: Constant Reactive Power 1: Volt-Var 2: Reserved | 0
0x0319 | 793 | 793 | 1 | RW | Power Change Mode | 功率变化模式 | enum16 |  |  |  | 0: Step 1: Ramp | 0
0x031A | 794 | 794 | 1 | RW | Active Power Regulation Mode | 有功功率调节模式 | enum16 |  |  |  | 0: Constant Active Power 1: Volt-Watt 2: Freq-Watt 3: Volt-Watt & Freq-Watt | 0
0x031B | 795 | 795 | 1 | RW | Grid voltage unbalance detect function | 电网电压不平衡检测使能 | enum16 |  |  |  | 0: Disabled 2: Enabled | 1
0x031C | 796 | 796 | 1 | RW | Continuous over voltage detect function | 连续过压检测使能 | enum16 |  |  |  | 0: Disabled 1: Enabled | 1
0x031D | 797 | 797 | 1 | RW | Grid detect in grid-tied mode function | 并网开机电网检测使能 | enum16 |  |  |  | 0: Disabled 0: Enabled | 1
0x031E | 798 | 798 | 1 | RW | Neutral wire floating detect function | 缺N检测使能 | enum16 |  |  |  | 0: Disabled 1: Enabled | 1
0x0328 | 808 | 808 | 1 | RW | Float charging voltage | 浮充电压（仅铅酸），若为锂电，需要和809设置为同一值 | uint16 | V |  | ×10 | 200.0~800.0V | 550V
0x0329 | 809 | 809 | 1 | RW | Slow charging volage |  | uint16 | V |  | ×10 | 200.0~800.0V | 550V
0x032A | 810 | 810 | 1 | RW | Current from slow charging to float charging |  | uint16 | A |  | ×10 | 0.0~90.0A | 10A
0x032B | 811 | 811 | 1 | RW | Max charging current |  | uint16 | A |  | ×10 | 0.0~90.0A | 90A
0x032C | 812 | 812 | 1 | RW | Max discharging current |  | uint16 | A |  | ×10 | 0.0~90.0A | 90A
0x032D | 813 | 813 | 1 | RW | Lower voltage limit of battery protection |  | uint16 | V |  | ×10 | 200.0~800.0V | 200V
0x032E | 814 | 814 | 1 | RW | Upper voltage limit of battery protection |  | uint16 | V |  | ×10 | 200.0~800.0V | 600V
0x033C | 828 | 828 | 1 | RW | High-Voltage Range 1 Ride-Tru Voltage (%Vnominal) | 高压1段穿越幅值(额定电压的系数) | uint16 | V | 1.10~1.20，默认1.10，*100下发 | ×100 | 1.1~1.2 | 1.1
0x033D | 829 | 829 | 1 | RW | High-Voltage Range 2 Ride-Tru Voltage (%Vnominal) | 高压2段穿越幅值(额定电压的系数) | uint16 | V | 1.10~1.20，默认1.20，*100下发 | ×100 | 1.1~1.2 | 1.2
0x033E | 830 | 830 | 1 | RW | Low-Voltage Range 1 Ride-Tru Voltage (%Vnominal) | 低压1段穿越幅值(额定电压的系数) | uint16 | V | 0.50~0.88，默认0.80，*100下发 | ×100 | 0.5~0.88 | 0.8
0x033F | 831 | 831 | 1 | RW | Low-Voltage Range 2 Ride-Tru Voltage (%Vnominal) | 低压2段穿越幅值(额定电压的系数) | uint16 | V | 0.50~0.88，默认0.60，*100下发 | ×100 | 0.5~0.88 | 0.6
0x0340 | 832 | 832 | 1 | RW | Low-Voltage Range 3 Ride-Tru Voltage (%Vnominal) | 低压3段穿越幅值(额定电压的系数) | uint16 | V | 0.40-0.50，默认0.50，*100下传 | ×100 | 0.4~0.5 | 0.5
0x0341 | 833 | 833 | 1 | RW | High-Frequency Range 1 Ride-Tru Frequency | 过频1段穿越幅值 | int16 | Hz | 1~6Hz，默认3Hz，*100下发 | ×100 | 1~6Hz | 3Hz
0x0342 | 834 | 834 | 1 | RW | High-Frequency Range 2 Ride-Tru Frequency | 过频2段穿越幅值 | int16 | Hz | 2~6Hz，默认5Hz，*100下发 | ×100 | 2~6Hz | 5Hz
0x0343 | 835 | 835 | 1 | RW | Low-Frequency Range 1 Ride-Tru Frequency | 欠频1段穿越幅值 | uint16 | V | -10~-0.1Hz，默认-3Hz，*100下发 | ×100 | -10~+0.1Hz | -3Hz
0x0344 | 836 | 836 | 1 | RW | Low-Frequency Range 2 Ride-Tru Frequency | 欠频2段穿越幅值 | uint16 | V | -10~-0.1Hz，默认-10Hz，*100下发 | ×100 | -10~+0.1Hz | -10Hz
0x0345 | 837 | 837 | 1 | RW | High-Voltage Range 1 Ride-Tru Until | 高压1段穿越时间 | uint16 | S | 0.08-12.00s，默认12.00，*100下传 | ×100 | 0.08~12s | 0
0x0346 | 838 | 838 | 1 | RW | High-Voltage Range 2 Ride-Tru Until | 高压2段穿越时间 | uint16 | S | 0.08-0.16s，默认0.1，*100下传 | ×100 | 0.08~0.16s | 1
0x0347 | 839 | 839 | 1 | RW | Low-Voltage Range 1 Ride-Tru Until | 低压1段穿越时间 | uint16 | S | 20.00-50.00s，默认20.00，*100下传 | ×100 | 20~50s | 0
0x0348 | 840 | 840 | 1 | RW | Low-Voltage Range 2 Ride-Tru Until | 低压2段穿越时间 | uint16 | S | 10.00-50.00s，默认10.00，*100下传 | ×100 | 10~50s | 0
0x0349 | 841 | 841 | 1 | RW | Low-Voltage Range 3 Ride-Tru Until | 低压3段穿越时间 | uint16 | S | 0.08-21.00s，默认0.5，*100下传 | ×100 | 0.08~21s | 5
0x034A | 842 | 842 | 1 | RW | High-Frequency Range 1 Ride-Tru Until | 过频1段穿越时间 | uint16 | S | 20-1000.00s，默认20.00，*10下传 | ×10 | 20~1000s | 0
0x034B | 843 | 843 | 1 | RW | High-Frequency Range 2 Ride-Tru Until | 过频2段穿越时间 | uint16 | S | 0-1000.00s，默认0.1，*10下传 | ×10 | 0~1000s | 1
0x034C | 844 | 844 | 1 | RW | Low-Frequency Range 1 Ride-Tru Until | 欠频1段穿越时间 | int16 | S | 20-1000.00s，默认20.00，*10下传 | ×10 | 20~1000s | 0
0x034D | 845 | 845 | 1 | RW | Low-Frequency Range 2 Ride-Tru Until | 欠频2段穿越时间 | int16 | S | 0-1000.00s，默认0.1，*10下传 | ×10 | 0~1000s | 1
0x034E | 846 | 846 | 1 | RW | Return-to-Service Frequency Ceiling | 恢复并网上限频率 | int16 | Hz | 0.1Hz～1Hz，默认0.1Hz，*100下发 | ×100 | 0.1~1Hz | 1Hz
0x034F | 847 | 847 | 1 | RW | Return-to-Service Frequency Floor | 恢复并网下限频率 | int16 | Hz | -1Hz～-0.1Hz，默认-0.1Hz，*100下发 | ×100 | -0.1~-1Hz | 1Hz
0x0350 | 848 | 848 | 1 | RW | Volt-Var reference voltage Vref | 电压无功调节参考电压Vref | uint16 |  | 0.95~1.05，默认1，*100下传 | ×100 | 0.95~1.05 | 1
0x0351 | 849 | 849 | 1 | RW | Volt-Var V1: Voltage at Q1 | 电压无功调节点V1 | uint16 |  | 0.82~1.03，默认0.92，*100下传 | ×100 | 0.82~1.03 | 92
0x0352 | 850 | 850 | 1 | RW | Volt-Var V2: Voltage at Q2 | 电压无功调节点V2 | uint16 |  | 0.95~1.05，默认0.98，*100下传 | ×100 | 0.95~1.05 | 98
0x0353 | 851 | 851 | 1 | RW | Volt-Var V3: Voltage at Q3 | 电压无功调节点V3 | uint16 |  | 1.00~1.05，默认1.02，*100下传 | ×100 | 1~1.05 | 2
0x0354 | 852 | 852 | 1 | RW | Volt-Var V4: Voltage at Q4 | 电压无功调节点V4 | uint16 |  | 1.02~1.18，默认1.06，*100下传 | ×100 | 1.02~1.18 | 6
0x0355 | 853 | 853 | 1 | RW | Max Capacitive Reactive Power Q1 | 最大容性无功调节量Q4 | uint16 |  | 0~0.6额定无功，默认0.3，*100下传 | ×100 | 0~0.6 | 3
0x0356 | 854 | 854 | 1 | RW | Initial Capacitive Reactive Power Q2 | 初始容性无功调节量Q3 | uint16 |  | 0~0.6额定无功，默认0，*100下传 | ×100 | 0~0.6 | 0
0x0357 | 855 | 855 | 1 | RW | Initial Inductive Reactive Power Q3 | 初始感性无功调节量Q2 | uint16 |  | 0~0.6额定无功，默认0，*100下传 | ×100 | 0~0.6 | 0
0x0358 | 856 | 856 | 1 | RW | Max Inductive Reactive Power Q4 | 最大感性无功调节量Q1 | uint16 |  | 0~0.6额定无功，默认0.3，*100下传 | ×100 | 0~0.6 | 0.3
0x0359 | 857 | 857 | 1 | RW | Settling Time of Volt-Watt (HECO SRD) | 电压无功调节反应时间 | uint16 | s | 1-90s，默认10s，*100下传 | ×100 | 1~90s | 10s
0x035E | 862 | 862 | 1 | RW | Volt-Watt Adjustment range of the start of active power reduction -Vstart | 过压降有功起始调节点V1 | uint16 |  | 1.03~1.1，默认1.06，*100下传 | ×100 | 1.03~1.1 | 1.06
0x035F | 863 | 863 | 1 | RW | Volt-Watt Adjustment range of the stop of active power reduction -Vstop | 过压降有功终止调节点V2 | uint16 |  | 1.04~1.1，默认1.1，*100下传 | ×100 | 1.04~1.1 | 1.1
0x0360 | 864 | 864 | 1 | RW | Volt-Watt Start Power P1 | 过压降有功起始功率P1 | uint16 |  | 0.00-1.00*当前有功，默认1，*100下传 | ×100 | 0~1 | 1
0x0361 | 865 | 865 | 1 | RW | Volt-Watt Stop Power P2 | 过压降有功终止功率P2 | uint16 |  | 0.00-1.00*当前有功，默认0，*100下传 | ×100 | 0.00~1.00 | 0
0x0362 | 866 | 866 | 1 | RW | Volt-Watt Delay before return to normal operation | 过压降有功恢复延时 | uint16 | s | 3~90s，默认60s，*100下传 | ×100 | 3~90s | 60s
0x0363 | 867 | 867 | 1 | RW | Volt-Watt settling time | 过压降有功反应时间 | uint16 | s | 0.5-60s，默认10s，*100下传 | ×100 | 0.5~60s | 10s
0x0364 | 868 | 868 | 1 | RW | Freq-Watt Start Frequency | 过频降有功调节点 | uint16 |  | 0.1-1Hz，默认0.1，*100下发 | ×100 | 0.1~1Hz | 0.1
0x0365 | 869 | 869 | 1 | RW | Freq-Watt Slope of the active power response to changes in frequency | 过频降有功调节斜率 | uint16 |  | 0.02~0.07，默认0.05，*100下传 | ×100 | 0.02~0.07 | 0.05
0x036C | 876 | 876 | 1 | RW | Soft-Start Ramp Rate | 软启功率变化速率 | uint16 |  |  | ×1000 | 0.001~1 Pnominal/s | 2
0x036D | 877 | 877 | 1 | RW | Ramp Rate | 功率变化速率 | uint16 |  |  | ×1000 | 0.01~2 Pnominal/s
0x036E | 878 | 878 | 1 | RW | Target PF | 功率因数设置 | uint16 |  |  | ×100 | -1~-0, inductive 1~0, capacitive | 1
0x036F | 879 | 879 | 1 | RW | Watt-PF P1(%Pnominal) | 有功调节功率因数有功调节点P1 | uint16 |  | 0.20~1.00*额定有功,默认0.20*额定有功,*100下传 | ×100 | 0.2~1 | 0.2
0x0370 | 880 | 880 | 1 | RW | Watt-PF P2(%Pnominal) | 有功调节功率因数有功调节点P2 | uint16 |  | 0.20~1.00*额定有功,默认0.50*额定有功,*100下传 | ×100 | 0.2~1 | 0.5
0x0371 | 881 | 881 | 1 | RW | Watt-PF P3(%Pnominal) | 有功调节功率因数有功调节点P3 | uint16 |  | 0.20~1.00*额定有功,默认0.70*额定有功,*100下传 | ×100 | 0.2~1 | 0.7
0x0372 | 882 | 882 | 1 | RW | Watt-PF P4(%Pnominal) | 有功调节功率因数有功调节点P4 | uint16 |  | 0.20~1.00*额定有功,默认1.00*额定有功,*100下传 | ×100 | 0.2~1 | 1
0x0373 | 883 | 883 | 1 | RW | PF1 | 功率因数调节点PF1 | int16 |  | -0.90~0.90,默认1,*100下传 | ×100 | -0.9~0.9 | 1
0x0374 | 884 | 884 | 1 | RW | PF2 | 功率因数调节点PF2 | int16 |  | -0.90~0.90,默认1,*100下传 | ×100 | -0.9~0.9 | 1
0x0375 | 885 | 885 | 1 | RW | PF3 | 功率因数调节点PF3 | int16 |  | -0.90~0.90,默认-0.96,*100下传 | ×100 | -0.9~0.9 | -0.96
0x0376 | 886 | 886 | 1 | RW | PF4 | 功率因数调节点PF4 | int16 |  | -0.90~0.90,默认-0.90,*100下传 | ×100 | -0.9~0.9 | -0.9
0x0FA1 | 4001 | 4006 | 6 | W | Time setting - Year\Month\Day\Hour\Minute\Second |  | uint16 | [5 empty] | YYYYMMDDHHmmss
0xF001 | 61441 | 61442 | 1 | R | Battery total voltage |  | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF002 | 61442 | 61443 | 1 | R | Battery total current |  | int16 | A |  |  |  |  | BMS protocol for Vendor A
0xF003 | 61443 | 61444 | 1 | R | Battery SOC |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF004 | 61444 | 61445 | 1 | R | Battery SOH |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF005 | 61445 | 61446 | 1 | R | Battery status bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF006 | 61446 | 61447 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF007 | 61447 | 61448 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF008 | 61448 | 61449 | 1 | R | Battery error bits |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF009 | 61449 | 61450 | 1 | R | Min temperature |  | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00A | 61450 | 61451 | 1 | R | Min temperature index |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF00B | 61451 | 61452 | 1 | R | Max temperature |  | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00C | 61452 | 61453 | 1 | R | Max temperature index |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF00D | 61453 | 61454 | 1 | R | Average temperature |  | int16 | C |  |  |  |  | BMS protocol for Vendor A
0xF00E | 61454 | 61455 | 1 | R | Average voltage |  | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF00F | 61455 | 61456 | 1 | R | Min voltage |  | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF010 | 61456 | 61457 | 1 | R | Min voltage index |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF011 | 61457 | 61458 | 1 | R | Max voltage |  | uint16 | V |  |  |  |  | BMS protocol for Vendor A
0xF012 | 61458 | 61459 | 1 | R | Max voltage index |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF013 | 61459 | 61460 | 1 | R | Max Allow charge current |  | uint16 | A |  |  |  |  | BMS protocol for Vendor A
0xF014 | 61460 | 61461 | 1 | R | Max Allow discharge current |  | uint16 | A |  |  |  |  | BMS protocol for Vendor A
0xF015 | 61461 | 61462 | 1 | R | BMS firmware version_LMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF016 | 61462 | 61463 | 1 | R | BMS firmware version_BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF017 | 61463 | 61464 | 1 | R | BMS firmware version_Top BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF018 | 61464 | 61465 | 1 | R | BMS hardware version_LMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF019 | 61465 | 61466 | 1 | R | BMS hardware version_BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01A | 61466 | 61467 | 1 | R | BMS hardware version_Top BMU |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01B | 61467 | 61468 | 1 | R | 1~16 Cluster status |  | uint16 | [5 empty] | BMS protocol for Vendor A
0xF01C | 61468 | 61469 | 1 | R | 17~20 Cluster status |  | uint16 | [5 empty] | BMS protocol for Vendor A
Operation enum16 list
enum16 | St |  |  |  | OFF | Off | 1
enum16 | St |  |  |  | SLEEPING | Sleeping | 2
enum16 | St |  |  |  | STARTING | Starting | 3
enum16 | St |  |  |  | MPPT | MPPT | 4
enum16 | St |  |  |  | THROTTLED | Throttled | 5
enum16 | St |  |  |  | SHUTTING_DOWN | Shutting down | 6
enum16 | St |  |  |  | FAULT | Fault | 7
enum16 | St |  |  |  | STANDBY | Standby | 8
enum16 | St |  |  |  | STARTED | Started | 9
Event bitfield32 list
bitfield32 | Evt1 |  |  |  | GROUND_FAULT | Ground fault | 0
bitfield32 | Evt1 |  |  |  | DC_OVER_VOLT | DC over voltage | 1
bitfield32 | Evt1 |  |  |  | AC_DISCONNECT | AC disconnect open | 2
bitfield32 | Evt1 |  |  |  | DC_DISCONNECT | DC disconnect open | 3
bitfield32 | Evt1 |  |  |  | GRID_DISCONNECT | Grid shutdown | 4
bitfield32 | Evt1 |  |  |  | CABINET_OPEN | Cabinet open | 5
bitfield32 | Evt1 |  |  |  | MANUAL_SHUTDOWN | Manual shutdown | 6
bitfield32 | Evt1 |  |  |  | OVER_TEMP | Over temperature | 7
bitfield32 | Evt1 |  |  |  | OVER_FREQUENCY | Frequency above limit | 8
bitfield32 | Evt1 |  |  |  | UNDER_FREQUENCY | Frequency under limit | 9
bitfield32 | Evt1 |  |  |  | AC_OVER_VOLT | AC Voltage above limit | 10
bitfield32 | Evt1 |  |  |  | AC_UNDER_VOLT | AC Voltage under limit | 11
bitfield32 | Evt1 |  |  |  | BLOWN_STRING_FUSE | Blown String fuse on input | 12
bitfield32 | Evt1 |  |  |  | UNDER_TEMP | Under temperature | 13
bitfield32 | Evt1 |  |  |  | MEMORY_LOSS | Generic Memory or Communication error (internal) | 14
bitfield32 | Evt1 |  |  |  | HW_TEST_FAILURE | Hardware test failure | 15

## BMS Protocol
| Start | End | Size | Access | Register Name | Type | Units | Comments | remarks
0x00A8 | 168 | 168 | 1 | W | D.C._Voltage | uint16 | V | D.C. Voltage | BMS protocol for Vendor B
0x00A9 | 169 | 169 | 1 | W | D.C._Voltage_SF | sunssf | SF | D.C. Voltage SF | BMS protocol for Vendor B
0x00AA | 170 | 170 | 1 | W | D.C._Current | uint16 | A | D.C. Current | BMS protocol for Vendor B
0x00AB | 171 | 171 | 1 | W | D.C._Current_SF | sunssf | SF | D.C. Current SF | BMS protocol for Vendor B
0x00AC | 172 | 172 | 1 | W | average_temp | uint16 | C | average temp | BMS protocol for Vendor B
0x00AD | 173 | 173 | 1 | W | average_temp_SF | sunssf | SF | average temp SF | BMS protocol for Vendor B
0x00AE | 174 | 174 | 1 | W | max_temp | uint16 | C | max temp | BMS protocol for Vendor B
0x00AF | 175 | 175 | 1 | W | max_temp_SF | sunssf | SF | max temp SF | BMS protocol for Vendor B
0x00B0 | 176 | 176 | 1 | W | min_Temp | uint16 | C | min Temp | BMS protocol for Vendor B
0x00B1 | 177 | 177 | 1 | W | min_Temp_SF | sunssf | SF | min Temp SF | BMS protocol for Vendor B
0x00B2 | 178 | 178 | 1 | W | max_cell_volt | uint16 | V | max cell volt | BMS protocol for Vendor B
0x00B3 | 179 | 179 | 1 | W | max_cell_volt_SF | sunssf | SF | max cell volt SF | BMS protocol for Vendor B
0x00B4 | 180 | 180 | 1 | W | min_cell_volt | uint16 | V | min cell volt | BMS protocol for Vendor B
0x00B5 | 181 | 181 | 1 | W | min_cell_volt_SF | sunssf | SF | min cell volt SF | BMS protocol for Vendor B
0x00B6 | 182 | 182 | 1 | W | average_cell_volt | uint16 | V | average cell volt | BMS protocol for Vendor B
0x00B7 | 183 | 183 | 1 | W | average_cell_volt_SF | sunssf | SF | average cell volt SF | BMS protocol for Vendor B
0x00B8 | 184 | 184 | 1 | W | soc | uint16 |  | soc | BMS protocol for Vendor B
0x00B9 | 185 | 185 | 1 | W | soc_SF | sunssf | SF | soc SF | BMS protocol for Vendor B
0x00BA | 186 | 186 | 1 | W | soh | uint16 |  | soh | BMS protocol for Vendor B
0x00BB | 187 | 187 | 1 | W | soh_SF | sunssf | SF | soh SF | BMS protocol for Vendor B
0xF001 | 61441 | 61442 | 1 | W | Battery total voltage | uint16 | V |  | BMS protocol for Vendor A
0xF002 | 61442 | 61443 | 1 | W | Battery total current | int16 | A |  | BMS protocol for Vendor A
0xF003 | 61443 | 61444 | 1 | W | Battery SOC | uint16 |  |  | BMS protocol for Vendor A
0xF004 | 61444 | 61445 | 1 | W | Battery SOH | uint16 |  |  | BMS protocol for Vendor A
0xF005 | 61445 | 61446 | 1 | W | Battery status bits | uint16 |  |  | BMS protocol for Vendor A
0xF006 | 61446 | 61447 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF007 | 61447 | 61448 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF008 | 61448 | 61449 | 1 | W | Battery error bits | uint16 |  |  | BMS protocol for Vendor A
0xF009 | 61449 | 61450 | 1 | W | Min temperature | int16 | C |  | BMS protocol for Vendor A
0xF00A | 61450 | 61451 | 1 | W | Min temperature index | uint16 |  |  | BMS protocol for Vendor A
0xF00B | 61451 | 61452 | 1 | W | Max temperature | int16 | C |  | BMS protocol for Vendor A
0xF00C | 61452 | 61453 | 1 | W | Max temperature index | uint16 |  |  | BMS protocol for Vendor A
0xF00D | 61453 | 61454 | 1 | W | Average temperature | int16 | C |  | BMS protocol for Vendor A
0xF00E | 61454 | 61455 | 1 | W | Average voltage | uint16 | V |  | BMS protocol for Vendor A
0xF00F | 61455 | 61456 | 1 | W | Min voltage | uint16 | V |  | BMS protocol for Vendor A
0xF010 | 61456 | 61457 | 1 | W | Min voltage index | uint16 |  |  | BMS protocol for Vendor A
0xF011 | 61457 | 61458 | 1 | W | Max voltage | uint16 | V |  | BMS protocol for Vendor A
0xF012 | 61458 | 61459 | 1 | W | Max voltage index | uint16 |  |  | BMS protocol for Vendor A
0xF013 | 61459 | 61460 | 1 | W | Max Allow charge current | uint16 | A |  | BMS protocol for Vendor A
0xF014 | 61460 | 61461 | 1 | W | Max Allow discharge current | uint16 | A |  | BMS protocol for Vendor A
0xF015 | 61461 | 61462 | 1 | W | BMS firmware version_LMU | uint16 |  |  | BMS protocol for Vendor A
0xF016 | 61462 | 61463 | 1 | W | BMS firmware version_BMU | uint16 |  |  | BMS protocol for Vendor A
0xF017 | 61463 | 61464 | 1 | W | BMS firmware version_Top BMU | uint16 |  |  | BMS protocol for Vendor A
0xF018 | 61464 | 61465 | 1 | W | BMS hardware version_LMU | uint16 |  |  | BMS protocol for Vendor A
0xF019 | 61465 | 61466 | 1 | W | BMS hardware version_BMU | uint16 |  |  | BMS protocol for Vendor A
0xF01A | 61466 | 61467 | 1 | W | BMS hardware version_Top BMU | uint16 |  |  | BMS protocol for Vendor A
0xF01B | 61467 | 61468 | 1 | W | 1~16 Cluster status | uint16 |  |  | BMS protocol for Vendor A
0xF01C | 61468 | 61469 | 1 | W | 17~20 Cluster status | uint16 |  |  | BMS protocol for Vendor A
BMS frame format
BMS communication mplementing RS485, the baud rate is 19200bps or 9600bps(default), verification: Modbus RTU Crc16
Vendor B protocol is only for transferring the data from BMS via RS485 to EMS via Ethernet, no protection will be applied by inverter. Vendor A protocol provides protection and status display by inverter Protocol for Vendor A is Strongly RECOMMENDED
SF(Scale Factor) is defined by Sunspec & MESA Actual value= Register value×10(SF)
Sending broadcasting frame
Device address | Operation code | Register Starting Address H | Register Starting Address L | Data H | Data L | Verification
(L->H)
0x00 | 0x06 | 0x00 | 0xA8 | 0x00 | 0x03 | CRC
THERE WILL BE NO Response frame

## Status and Fault Listing
32 | Bit0 Fault status
32 | Bit1 Alert status
32 | Bit2 On/Offstatus
32 | Bit3 On-grid
32 | Bit4 Off-grid
32 | Bit5 Reserved
32 | Bit6 Reserved
32 | Bit7 Reserved
32 | Bit8-15 Reserved
33 | Bit0-7 Reserved
33 | Bit8 Islanding enabled
33 | Bit9-15 Reserved
34 | Bit0-7 Reserved
34 | Bit8-15 Reserved
35 | Bit0-7 Reserved
35 | Bit8-15 Reserved
36 | bit0 AC OVP
36 | Bit1 AC UVP
36 | Bit2 AC OFP
36 | Bit3 AC UFP
36 | Bit4 Grid voltage unbalance.
36 | Bit5 Grid phase reverse
36 | Bit6 Islanding
36 | Bit7 On/off grid switching error
36 | Bit8 Output grounding error
36 | Bit9 Output current abnormal
36 | Bit10 Grid phase lock fails
36 | Bit11 Internal air over-temp
36 | Bit12 允许并网条件判断超时
36 | Bit13-15 Reserved
37 | Bit0 EPO
37 | bit1 HMI parameters fault
37 | Bit2 DSP version error
37 | Bit3 CPLD version error
37 | Bit4 Hardware Version error
37 | Bit5 Communication error
37 | Bit6 Aux power error
37 | Bit7-Fan failure
37 | Bit8 BUS over voltage
37 | Bit9 BUS low voltage
37 | Bit10 BUS voltage unbanlaced
37 | Bit11 AC soft start failure
37 | Bit12 Reserved
37 | Bit13 Output voltage abnormal.
37 | Bit14 Output current unbalanced
37 | Bit15 Over-temperature of heat sink
38 | Bit0 Output Overload
38 | Bit1 Reserved
38 | Bit2 AC breaker short-circuit.
38 | Bit3 Inverter start failure.
38 | Bit4 AC breaker is open.
38 | Bit5-15 Reserved
39 | Bit0 EE Reading error 1
39 | Bit1 EE Reading error 2
39 | Bit2 SPD failure
39 | Bit3 Inverter over load
39 | Bit4-15 Reserved
40 | bit0 DC charging
40 | bit1 DC discharging
40 | bit2 Battery fully charged
40 | bit3-Battery empty
40 | Bit4 Fault status
40 | Bit5 Alert status
40 | Bit6-15 Reserved
41 | Bit0-7 Reserved
41 | Bit8-15 Reserved
42 | Bit0-7 Reserved
42 | Bit8-15 Reserved
43 | Bit0-7 Reserved
43 | Bit8-15 Reserved
44 | Bit0 DC input OVP
44 | Bit1 DC input UVP
44 | Bit2 DC grounding error
44 | Bit3 BMS Alerts.
44 | Bit4-7 Reserved
44 | Bit8-15 Reserved
45 | bit0 DC soft-start fails.
45 | bit1 DC relay short-circuit.
45 | bit2 DC relay short-open
45 | Bit3 Battery power over load.
45 | Bit4 BUS start fails.
45 | Bit5-7 Reserved
45 | Bit8-15 Reserved
46 | Bit0-7 Reserved
46 | Bit8-15 Reserved
47 | Bit0 DC OCP
47 | Bit1-7 Reserved
47 | Bit8-15 Reserved
48-63 | Reserved